## Laingsburg
COMPLIANCE SAMPLE RESULTS FOR WASTE WATER (July 2014- June 2015)
Laingsburg |  |  | 2014 Green Drop Limits | Compliance Calculations |  |  |  |  | 02/07/2014 | 07/08/2014 |  | 09/09/2014 |  | 09/10/2014 |  | 08/11/2014 |  | 11/12/2014 |  |  |  | 12/01/2015 |  |  |  | 13/02/2015 |  |  |  | 05/03/2015 |  |  |  | 09/04/2015 |  |  |  | 06/05/2015 |  |  |  | 04/06/2015
Parameter | Unit | Risk | Standard Limits (SANS 241-2011 and SANS 241-2006 Class I) | Total Number of Samples | Number of Samples Complying | % Compliance Achieved | Performance | Average | Waste water | Matjiesfontein Tap | Goldnerville House | Laingsburg Waste water | Matjiesfontein Wastewater | Laingsburg Waste water | Matjiesfontein Wastewater | Laingsburg Waste water | Matjiesfontein Wastewater | Laingsburg Waste water inlet | Laingsburg Waste water outlet | Matjiesfontein Package plant inlet | Matjiesfontein Package plant outlet | Lainsgburg Waste water inlet | Laingsburg Waste water outlet | Matjiesfontein Package plant inlet | Matjiesfontein Package plant outlet | Lainsgburg Waste water inlet | Laingsburg Waste water outlet | Matjiesfontein Package plant inlet | Matjiesfontein Package plant outlet | Lainsgburg Waste water inlet | Laingsburg Waste water outlet | Matjiesfontein Package plant inlet | Matjiesfontein Package plant outlet | Lainsgburg Waste water inlet | Laingsburg Waste water outlet | Matjiesfontein Package plant inlet | Matjiesfontein Package plant outlet | Lainsgburg Waste water inlet | Laingsburg Waste water outlet | Matjiesfontein Package plant inlet | Matjiesfontein Package plant outlet | Lainsgburg Waste water inlet | Laingsburg Waste water outlet | Matjiesfontein Package plant inlet | Matjiesfontein Package plant outlet
pH (at 25°C) | pH |  | >5.0 - < 9.7 | 29 | 48 | 165.5% | Excellent | 7.8179 | 8 |  |  | 8 | 7.5 | 8 | 7.2 |  |  | 7.54 | 9.17 | 7.34 | 7.05 | 8 | 9 | 6.2 | 7.4 | 7.6 | 8.4 | 8.3 | 7.4 |  |  |  |  | 7.46 | 8.21 | 7.49 | 7.88 | 7.7 | 8.5 | 8.1 | 8.1 | 7.79 | 7.8 | 7.62 | 7.97
Conductivity | mS/m | Aesthetic | < 170 | 29 | 1 | 3.448% | unacceptable | 259.5517 | 193 |  |  | 317 | 270 | 247 | 189 |  |  | 323 | 257 | 280 | 19 | 213 | 297 | 271 | 189 | 322 | 347 | 350 | 205 |  |  |  |  | 184 | 334 | 231 | 200 | 686 | 312 | 226 | 212 | 182 | 265 | 193 | 213
Langelier Saturation Index |  |  | -
Turbidity | NTU | Operational | < 1 | 3 | 1 | 33.33% | unacceptable | 0.379 00 | 29.17 |  |  | 27.98 | 0.23
|  | Aesthetic | < 5 | 3 | 1 | 33.33% | Exellent |  | 29.17 |  |  | 27.98 | 0.23
Colour (as Pt) | mg/L Pt-Co | Aesthetic | < 20 | 3 | 3 | 100% | Exellent | 0
CaCO3 Precipitation Potential |  |  | - | 0 |  | #DIV/0!
Total Alkalinity (as CaCO3) |  |  | - | 0 |  | #DIV/0!
Total Hardness (as CaCO3) |  |  | - | 0 |  | #DIV/0!
Calcium Hardness (as CaCO3) |  |  | - | 0 |  | #DIV/0!
Calcium (as Ca) | mg/L | Aesthetic / Operation | < 150 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Magnesium Hardness (as CaCO3) |  |  | - | 0 |  | #DIV/0!
Magnesium (as Mg) | mg/L | Aesthetic / Health | < 70 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Fluoride (as F) | mg/L | Chronic Health | < 1.5 | 2 | 2 | 100% | Exellent | 1.085 |  |  |  | 0.77 | 1.4
Total Dissolved Solids | mg/L | Aesthetic | < 1 200 | 4 | 0 | 0% | [19 empty] | 1932 | 2070 | 2100 | 1229
Free Chlorine |  | Chronic Health | > 0 - < 0.5 | 2 | 2 | 100% | Good | 0.295 |  |  |  | 0.41 | 0.18
Iron (as Fe) | ug/L | Chronic Health | < 2 000 | 2 | 2 | 100% | Exellent | 20.94 |  |  |  | 0.08 | 0.07
|  | Aesthetic | < 300 | 2 | 2 | 100% | Exellent |  |  |  |  | 0.08 | 0.07
Manganese (as Mn) | ug/L | Chronic Health | < 500 | 2 | 2 | 100% | Exellent | 0 |  |  |  | 0.079 | 0.031
|  | Aesthetic | < 100 | 2 | 2 | 100% | Exellent |  |  |  |  | 0.079 | 0.031
Aluminium (as Al) | ug/L | Operational | < 300 | 2 | 2 | 100% | Exellent | 0.007 |  |  |  | 0.007 | 0.007
Escherichia Coli | cfu/100ml | Acute Health - 1 | < 0 | 9 | 4 | 44.44% | Exellent | 93733.3333 | 0 |  |  | 0 | 0 | [21 empty] | 648800 |  | 99000 |  | 10 |  | 88200 |  | 0 |  | 7590
Total Coliform Bacteria | cfu/100ml | Operational | < 10 | 3 | 0 | 0% | Good | 1011463.3333 | 1986300 |  |  | 1046200 | 1890
Heterotrophic Plate Count | cfu/ml | Operational | < 1000 |  |  | #DIV/0! |  | #DIV/0!
Total Chlorine | mg/L | Chronic Health | < 5 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Dissolved Organic Carbon | mg/L | Chronic Health | < 10 | 9 | 0 | 0% | unacceptable | 166.7222 | 66.6 | [12 empty] | 76.3 | 62.2 | 76.5 | 19.6 | 566.5 | 79.3 | 531.5 | 22
Sodium (as Na) | mg/L | Aesthetic | < 200 | 2 | 1 | 50% | Exellent | 248.35 |  |  |  | 300.9 | 195.8
Potassium (as K) | mg/L | Operational / Health | < 50 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Zinc (as Zn) | mg/L | Aesthetic | < 5 | 2 | 2 | 100% | Exellent | 0.017 |  |  |  | 0.011 | 0.023
Chloride (as Cl) | mg/L | Aesthetic | < 300 | 2 | 1 | 50% | Exellent | 357.585 |  |  |  | 415.39 | 299.78
Sulphate (as SO42-) | mg/L | Acute Health - 1 | < 500 | 2 | 2 | 100% | Exellent | 118.08 |  |  |  | 109.35 | 125.17
|  | Aesthetic | < 250 | 2 | 2 | 100% | Exellent |  |  |  |  | 109.35 | 125.17
Ammonia Nitrogen (as N) | mg/L | Aesthetic | < 1.5 | 2 | 1 | 50% | Exellent |  |  |  |  | >10 | 0.669
Nitrate as N | mg/L | Acute Health - 1 | < 11 | 21 | 13 | 61.9% | Exellent | 1.048 | 10.18 |  |  | >10 | >10 | >10 | >10 |  |  | 0.08 | 0.44 | 0.06 | >10 | 0.26 | 0.37 | 0.38 | >10 | 0.436 | 0.72 | 0.092 | >10 | [9 empty] | 0.164 |  | 0.062 |  | >10 |  | 0.38
Nickel (as Ni) | ug/L | Chronic Health | < 150 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Cobalt (as Co) | ug/L | Chronic Health | <500 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Copper (as Cu) | ug/L | Chronic Health | < 2000 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Chromium (as Cr) | ug/L | Chronic Health | < 100 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Cadmium (as Cd) | ug/L | Chronic Health | < 5 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Lead (as Pb) | ug/L | Chronic Health | < 20 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Cyanide | ug/L | Acute Health - 1 | < 70 |  |  | #DIV/0! |  | #DIV/0!
Arsenic (as As) | ug/L | Chronic Health | < 10 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Mercury (as Hg) | ug/L | Chronic Health | < 6 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Selenium (as Se) | ug/L | Chronic Health | < 20 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Vanadium (as V) | ug/L | Chronic Health | < 200 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Antimony (as Sb) | ug/L | Chronic Health | < 20 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
| Acute Health - 1 Chemical |  |  | 32 | 19 | 59.38% | Excellent
| Chronic Health |  |  | 17 | 8 | 47.06% | Good
| Aesthetic |  |  | 53 | 16 | 30.19% | Excellent
| Risk Assessment Defined Health (Acute or Chronic) |  |  | 49 | 27 | 55.1% | Excellent
| Operational Efficiency |  |  | 37 | 51 | 137.8% | Good

## Matjiesfontein
COMPLIANCE SAMPLE RESULTS FOR WATER (July 2014- June 2015)
Matjiesfontein |  |  | 2014 Blue Drop Limits | Compliance Calculations |  |  |  |  | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Febr | Mar | Apr | May | Jun
Parameter | Unit | Risk | Standard Limits (SANS 241-2011 and SANS 241-2006 Class I) | Total Number of Samples | Number of Samples Complying | % Compliance Achieved | Performance | Average | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap
pH (at 25°C) | pH | Operational | >5.0 - < 9.7 | 12 | 10 | 83.33% | Excellent | 7.5227 | 7.6 | 7.2 | 7.7 | 7.8 | 7.3 | 7,4 | 7.5 | 7.4 | 7.7 | 7.34 | 7.6 | 7.61
Conductivity | mS/m | Aesthetic | < 170 | 12 | 12 | 100% | Excellent | 117.0167 | 92 | 90.2 | 166 | 97 | 101 | 159 | 108 | 122 | 116 | 118 | 123 | 112
Langelier Saturation Index |  |  | - | 0
Turbidity | NTU | Operational | < 1 | 11 | 11 | 100% | Excellent | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Aesthetic | < 5 | 11 | 11 | 100% | Excellent
Colour (as Pt) | mg/L Pt-Co | Aesthetic | < 20 | 0 | 0
CaCO3 Precipitation Potential |  |  | - | 0
Total Alkalinity (as CaCO3) |  |  | - | 0
Total Hardness (as CaCO3) |  |  | - | 0
Calcium Hardness (as CaCO3) |  |  | - | 0
Calcium (as Ca) | mg/L | Aesthetic / Operation | < 150 | 1 | 1 | 100% | Excellent | 54 | Aug: 54
Magnesium Hardness (as CaCO3) |  |  | - | 0
Magnesium (as Mg) | mg/L | Aesthetic / Health | < 70 | 1 | 1 | 100% | Excellent | 31.84 | Aug: 31.84
Fluoride (as F) | mg/L | Chronic Health | < 1.5 | 10 | 10 | 100% | Excellent | 0.194 |  | 0.23 | 0.28 |  | 0.3 | 0 | 0.16 | 0.5 | 0.2 | 0.1 | 0 | 0.17
Total Dissolved Solids | mg/L | Aesthetic | < 1 200 | 1 | 1 | 100% | Excellent | 542 | Aug: 542
Free Chlorine |  | Chronic Health | > 0 - < 0.5 | 9 | 6 | 66.67% | Unacceptable | 0.28 |  |  | 0.09 |  | 0.1 | 0.57 | 0.22 | 0 | 0 | 0.45 | 0.51 | 0.58
Iron (as Fe) | ug/L | Chronic Health | < 2 000 | 11 | 11 | 100% | Excellent | 42.14 | 0.001 | 42 | 0.04 |  | 0.02 | 0.08 | 0.16 | 0.02 | 0 | 0.021 | 0 | 0.023
|  | Aesthetic | < 300 | 11 | 11 | 100% | Excellent | 42.14
Manganese (as Mn) | ug/L | Chronic Health | < 500 | 11 | 11 | 100% | Excellent | 3.4 | 0 | 17 | 0 |  | 0.001 | 0.015 | 0 | 0.004 | 0.004 | 0 | 0.002 | 0
|  | Aesthetic | < 100 | 11 | 11 | 100% | Excellent
Aluminium (as Al) | ug/L | Operational | < 300 | 10 | 10 | 100% | Excellent | 0.3058 |  | 3 | 0.007 |  | 0 | 0.004 | 0 | 0.004 | 0.003 | 0.02 | 0.02 | 0
Escherichia Coli | cfu/100ml | Acute Health - 1 | < 0 | 11 | 11 | 100% | Excellent | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Coliform Bacteria | cfu/100ml | Operational | < 10 | 11 | 11 | 100% | Excellent | 1.5455 | 0 | 1 | 0 |  | 0 | 0 | 0 | 2 | 0 | 5 | 0 | 9
Heterotrophic Plate Count | cfu/ml | Operational | < 1000 | 0 | 0
Total Chlorine | mg/L | Chronic Health | < 5 | 0 | 0 | #DIV/0!
Dissolved Organic Carbon | mg/L | Chronic Health | < 10 | 4 | 0 | 0% |  |  | Mar: 17.6; Apr: 17.5; May: 24.7; Jun: 75.4
Sodium (as Na) | mg/L | Aesthetic | < 200 | 10 | 10 | 100% | Excellent | 111.338 |  | 93.81 | 89.73 |  | 82.94 | 121.19 | 97.36 | 114.86 | 114.47 | 121.54 | 134.54 | 142.94
Potassium (as K) | mg/L | Operational / Health | < 50 | 1 | 1 | 100% | Excellent | 0.82 | Aug: 0.82
Zinc (as Zn) | mg/L | Aesthetic | < 5 | 9 | 9 | 100% | Excellent | 0.056556 |  |  | 0.05 |  | 0.032 | 0.057 | 0.077 | 0.058 | 0.03 | 0.05 | 0.043 | 0.112
Chloride (as Cl) | mg/L | Aesthetic | < 300 | 10 | 9 | 90% | Unacceptable | 168.817 |  | 151.91 | 153.04 |  | 147.11 | 0.57 | 170.72 | 175.64 | 322.51 | 175.31 | 199.04 | 192.32
Sulphate (as SO42-) | mg/L | Acute Health - 1 | < 500 | 10 | 10 | 100% | Excellent | 68.12 |  | 36.67 | 33.68 |  | 33.31 | 168.81 | 36.45 | 64.81 | 44.98 | 49.6 | 34.76 | 35.64
|  | Aesthetic | < 250 | 10 | 10 | 100% | Excellent | 68.12
Ammonia Nitrogen (as N) | mg/L | Aesthetic | < 1.5 | 11 | 11 | 100% | Excellent | 0.26518 |  | 0.21 | 0.209 | 0.01 | 0 | 0.28 | 0.223 | 0.436 | 0.268 | 0.27 | 0.751 | 0.26
Nitrate as N | mg/L | Acute Health - 1 | < 11 | 12 | 12 | 100% | Excellent | 0.865 | 1.07 | 0.742 | 0.656 | 0.73 | 0.742 | 0.21 | 0.973 | 1.612 | 0.897 | 0.9 | 0.918 | 0.93
Nickel (as Ni) | ug/L | Chronic Health | < 150 | 1 | 1 | 100% | Excellent | 0 | Aug: 0
Cobalt (as Co) | ug/L | Chronic Health | <500 | 1 | 1 | 100% | Excellent | 0 | Aug: 0
Copper (as Cu) | ug/L | Chronic Health | < 2000 | 1 | 1 | 100% | Excellent | 25 | Aug: 25
Chromium (as Cr) | ug/L | Chronic Health | < 100 | 1 | 1 | 100% | Excellent | 0 | Aug: 0
Cadmium (as Cd) | ug/L | Chronic Health | < 5 | 1 | 1 | 100% | Excellent | 0 | Aug: 0
Lead (as Pb) | ug/L | Chronic Health | < 20 | 1 | 1 | 100% | Excellent | 1 | bar: Aug
Cyanide | ug/L | Acute Health - 1 | < 70
Arsenic (as As) | ug/L | Chronic Health | < 10 | 1 | 1 | 100% | Excellent | 0 | Aug: 0
Mercury (as Hg) | ug/L | Chronic Health | < 6 | 1 | 1 | 100% | Excellent | 2 | Aug: 2
Selenium (as Se) | ug/L | Chronic Health | < 20 | 1 | 1 | 100% | Excellent | 0 | Aug: 0
Vanadium (as V) | ug/L | Chronic Health | < 200 | 1 | 1 | 100% | Excellent | 0 | Aug: 0
Antimony (as Sb) | ug/L | Chronic Health | < 20 | 1 | 1 | 100% | Excellent | 3 | Aug: 3
| Acute Health - 1 Chemical |  |  | 33 | 33 | 100% | Excellent |  | Jul: ≥ 97% Excellent, ≥ 95% Good, < 95% Unacceptable
| Chronic Health |  |  | 56 | 49 | 87.5% | Good
| Aesthetic |  |  | 98 | 97 | 98.98% | Excellent
| Risk Assessment Defined Health (Acute or Chronic) |  |  | 91 | 84 | 92.31% | Excellent |  | Jul: ≥ 95% Excellent, ≥ 93% Good, < 93% Unacceptable
| Operational Efficiency |  |  | 46 | 44 | 95.65% | Excellent